## Zonal Calculator
Average Maintained Illumination Calculator Lumen Method
Room Information |  | Luminaire Information
Room Name |  | Luminaire Mfr.
Target Illuminance |  | Luminaire Catalog No.
Room Size (decimal feet) |  | No. Luminaires | 24
Length | 30 | Lamp Lumens | 5200
Width | 100 | Lamps per Luminaire | 1
Area | 3000 | Luminaire Lumens | 5200
Room Surface Reflectance |  | Coefficient of Utilization | 0.72
Ceiling | 0.5
Wall | 0.5 | Light Loss Factors
Floor | 0.2 | Non Recoverable
Cavity Heights (decimal feet) |  | Voltage | 1
Ceiling | 0 | Ballast | 1
Room | 9.5 | Thermal | 1
Floor | 2.5 | Recoverable
Room Cavity Ratio | 2.0583 | LDD | 0.95
|  | LLD | 0.9
|  | RSDD | 0.95
|  | Total Light Loss Factors | 0.81225
Maintained Illuminance
|  | Footcandles | Lumens
|  | 24.3285 | 261.7748
Enter required information in the blue fields. Red fields are automatically calculated.